## Schedule of Equipment
PANORAMA - Indoor Units Schedule:
S.N. | Building Unit | Room Name | System Name | Sensible Cooling Load (KW) | Total Cooling Load (KW) | Heating Load (KW) | Air Flow (L/s) | Cooling Conditions |  |  |  | Heating Conditions |  | Required Outdoor Air (L/s) | Mitsubushi Indoor Equipment Selection Data
[8 empty] | EDB | EWB | LDB | LWB | EDB | LDB |  | Indoor Quantity | FCU Selection | Selection (L/s) | Static Pressure Max. (Pa) | Sound Level (dBA) | Height (mm) | Length (mm) | Depth (mm) | Supply Outlet (mm) | Liquid (Inch) | Gas (Inch) | Weight (Kg)
1 | East Wing | Master Bedroom | FCU-EW-01 | 4.3 | 4.9 | 2.5 | 250 | 28.9 | 19.3 | 14.4 | 13.6 | 19 | 27.5 | 27 | 1 | FDUM71KXE6F | 317 / 250 / 167 | 100 Pa | 33 / 29 / 25 | 280 | 950 | 635 | to be checked | 3/8" | 5/8" | 34
2 | East Wing | Toilet Area | FCU-EW-02 | 2.2 | 2.4 | 0.6 | 150 | 26.4 | 18.4 | 14.4 | 13.7 | 20.2 | 23.5 | 8 | 1 | FDUM28KXE6F | 167 / 150 / 134 | 100 Pa | 32 / 29 / 26 | 280 | 750 | 635 | to be checked | 1/4" | 3/8" | 29
3 | East Wing | Open Office | FCU-EW-03 | 7.2 | 7.6 | 3.1 | 417 | 28.8 | 18.9 | 14.4 | 13.5 | 20.4 | 26.6 | 14 | 1 | FDUM112KXE6F | 467 / 417 / 317 | 100 Pa | 38 / 36 / 30 | 280 | 1370 | 740 | to be checked | 3/8" | 5/8" | 54
4 | East Wing | Basement MEDIA | FCU-EW-04 | 2.9 | 3.2 | 1.9 | 150 | 30.5 | 19.6 | 14.4 | 13.4 | 18.3 | 28.9 | 23 | 1 | FDK36KXZE1 | 184 / 167 / 134 / 117 | - | 40 / 38 / 33 | 290 | 870 | 230 | - | 1/4" | 1/2"
5 | Existing Dwelling | Entrance | FCU-ED-01 | 1.1 | 1.2 | 0.6 | 88 | 25.6 | 18.9 | 15.7 | 15.1 | 19.2 | 25.1 | 9
6 | Existing Dwelling | Family | FCU-ED-02 | 5 | 6.2 | 2.7 | 250 | 31 | 20.6 | 14.4 | 13.5 | 17.3 | 26.3 | 53 | 1 | FDUM90KXE6F | 317 / 250 / 167 | 100 Pa | 33 / 29 / 25 | 280 | 950 | 635 | to be checked | 3/8" | 5/8" | 34
7 | Existing Dwelling | Kitchen + Meal | FCU-ED-03 | 5.7 | 6.5 | 1.8 | 250 | 33.3 | 20.8 | 14.4 | 13.3 | 20.5 | 23.1 | 26.4 | 1 | FDUM90KXE6F | 317 / 250 / 167 | 100 Pa | 33 / 29 / 25 | 280 | 950 | 635 | to be checked | 3/8" | 5/8" | 34
8 | Existing Dwelling | Studio | FCU-ED-04 | 4.8 | 6.1 | 2.7 | 250 | 30.6 | 20.5 | 14.4 | 13.5 | 17.4 | 26.5 | 52 | 1 | FDUM90KXE6F | 317 / 250 / 167 | 100 Pa | 33 / 29 / 25 | 280 | 950 | 635 | to be checked | 3/8" | 5/8" | 34
9 | West Wing | Bedroom 2 | FCU-WW-01 | 2.7 | 3.1 | 1.3 | 150 | 29.5 | 19.6 | 14.4 | 13.5 | 19.7 | 26.8 | 11 | 1 | FDUM45KXE6F | 167 / 150 / 134 | 100 Pa | 32 / 29 / 26 | 280 | 750 | 635 | to be checked | 1/4" | 3/8" | 29
10 | West Wing | Bedroom 3 | FCU-WW-02 | 2.2 | 2.5 | 0.7 | 150 | 26.5 | 18.6 | 14.4 | 13.7 | 19.7 | 23.7 | 10 | 1 | FDUM28KXE6F | 167 / 150 / 134 | 100 Pa | 32 / 29 / 26 | 280 | 750 | 635 | to be checked | 1/4" | 3/8" | 29
11 | West Wing | Bedroom 4 | FCU-WW-03 | 2.2 | 2.5 | 0.8 | 150 | 26.6 | 18.6 | 14.4 | 13.7 | 19.9 | 24.2 | 10 | 1 | FDUM28KXE6F | 167 / 150 / 134 | 100 Pa | 32 / 29 / 26 | 280 | 750 | 635 | to be checked | 1/4" | 3/8" | 29
12 | West Wing | Bedroom 5 | FCU-WW-04 | 2.7 | 3 | 1.2 | 150 | 29.4 | 19.4 | 14.4 | 13.5 | 19.8 | 26.3 | 10 | 1 | FDUM45KXE6F | 167 / 150 / 134 | 100 Pa | 32 / 29 / 26 | 280 | 750 | 635 | to be checked | 1/4" | 3/8" | 29
13 | West Wing | Laundty + Hall Corridor | FCU-WW-05 | 2 | 2.4 | 0.8 | 150 | 25.7 | 18.5 | 14.4 | 13.8 | 19 | 23.6 | 17 | 1 | FDUM28KXE6F | 167 / 150 / 134 | 100 Pa | 32 / 29 / 26 | 280 | 750 | 635 | to be checked | 1/4" | 3/8" | 29
14 | West Wing | Rumpus + Hall Corridor | FCU-WW-06 | 8.8 | 10.1 | 5 | 500 | 29.2 | 19.5 | 14.4 | 13.6 | 16.8 | 25.1 | 122 | 2 | FDUM71KXE6F | 317 / 250 / 167 | 100 Pa | 33 / 29 / 25 | 280 | 950 | 635 | to be checked | 3/8" | 5/8" | 34
Not to be conditioned
Edited
Remarks:
1- The "Entrance" Space is to be inculded in Family and Studio Spaces.
PANORAMA - Outdoor Units Schedule:
S.N. | Building Unit | System Name | Total Cooling Load (KW) | Heating Load (KW) | Mitsubushi Outdoor Equipment Selection Data
[5 empty] | Nominal Cooling Capacity (kW) | Nominal Heating Capacity (kW) | Outdoor Unit Selection | Type | Refrigerant Type | Sound dBA | Height (mm) | Length (mm) | Depth (mm) | Liquid (Inch) | Elect.Input / Type | Power Consumption (kW) Cooling / Heating | Rated Current (A) Cooling / Heating | Refrigerant Type | Sound Level (dBA) | Liquid (Inch) | Gas (Inch) | Weight (Kg)
1 | East Wing | OU-01 | 15.7 | 7.5 | 22.4 | 22.4 | PUMY-P-VKM-A/YKM-A | Inverter | R410/2088 | 60 | 1505 | 970 | 370 | 3/8" | 3ph-380 , 415v - 50 Hz / Inverter | 5.6 kW / 4.8 kW | 9.2 A / 7.9 A | R410/2088 | 60 | 3/8" | 3/4" - 7/8" | 165
2 | Existing Dwelling | OU-02 | 20 | 7.8 | 22.4 | 22.4 | PUMY-P-VKM-A/YKM-A | Inverter | R410/2088 | 60 | 1505 | 970 | 370 | 3/8" | 3ph-380 , 415v - 50 Hz / Inverter | 5.6 kW / 4.8 kW | 9.2 A / 7.9 A | R410/2088 | 60 | 3/8" | 3/4" - 7/8" | 165
3 | West Wing | OU-03 | 21.2 | 9 | 22.4 | 22.4 | PUMY-P-VKM-A/YKM-A | Inverter | R410/2088 | 60 | 1505 | 970 | 370 | 3/8" | 3ph-380 , 415v - 50 Hz / Inverter | 5.6 kW / 4.8 kW | 9.2 A / 7.9 A | R410/2088 | 60 | 3/8" | 3/4" - 7/8" | 165
PANORAMA - Fans Schedule
S.N. | Floor | Space | System Name | System | Air Flow (cfm) | Static Pressure (Pa) | Preliminary Electrical Load (KW) | Type | Remarks
1 | East Wing | WC | EW-EF-01 | Exhaust | 25 | 100 |  | Ceiling Mounted
2 | East Wing | MEDIA - Basem. | EW-EF-02 | Exhaust | 140 | 100 |  | Ceiling Mounted
3 | Existing Dwelling | Cloak | ED-EF-01 | Exhaust | 25 | 100 |  | Ceiling Mounted
4 | Existing Dwelling | WC | ED-EF-02 | Exhaust | 25 | 100 |  | Ceiling Mounted
5 | West Wing | Toilet 1 | WW-EF-01 | Exhaust | 25 | 100 |  | Ceiling Mounted
6 | West Wing | Toilet 2 | WW-EF-02 | Exhaust | 25 | 100 |  | Ceiling Mounted
7 | West Wing | Toilet 3 | WW-EF-03 | Exhaust | 25 | 100 |  | Ceiling Mounted
8 | West Wing | Toilet 4 | WW-EF-04 | Exhaust | 25 | 100 |  | Ceiling Mounted
Remarks:
1- All fans shall be integrated with Back Draft Dampers.
2- The fans shall be connected with lighting switches, and supported by timer, to be turned off for at least in 30 seconds.